Introduction

AMT 105 and AMT 205 are two advanced, specialized products from Vebko, designed and manufactured to facilitate and enhance the testing and evaluation of relays and protective equipment in power systems. Leveraging modern hardware and software technologies, these devices enable engineers and protection specialists to perform a wide range of precise, reliable tests in accordance with international standards. Both units are equipped with configurable voltage and current sources, binary inputs/outputs, and analog channels, allowing users to fully simulate real operating conditions of relays and protection systems—so tests are carried out with high accuracy under field-like conditions.

Compared with the AMT 105, the AMT 205 is technically more advanced and, thanks to its higher output power, faster sampling rates, wider measurement range, and greater signal-control accuracy, is an ideal choice for heavier projects and more complex tests. A standout advantage of the AMT 205 is its support for modern international protocols and standards such as IEC 61850, which allows users to perform advanced tests based on digital communication networks with ease.

Complementing this powerful hardware, Vebko provides its dedicated AMPRO software, which handles control, monitoring, and automation of the testing process. With a user interface that is both simple and professional, AMPRO supervises every stage of the test in real time and manages the device outputs according to the defined scenarios.

Electrical and Physical Specifications

AMT105

AMT205

4 Voltage Outputs

DC Supply

4 Binary Outputs

DC/AC Analog Input

On/Off Key

Multifunctional Inputs

Combination Connector

6 Current Outputs

4 Binary Outputs

6 Voltage Outputs or 
5 Voltage Output & 1 DC Supply

DC/AC Analog Input

6 Current Outputs

On/Off Key

Combination Connector

Multifunctional Inputs

Wifi Antenna

USB Host

RS232

Earth

USB Debug

LAN

LAN/Wifi Switching

USB

Gps

Earth

USB-A

Power Input 
85 to 250 V AC 
100 to 330 V DC 
Max 10 A 
Frequency 47/63 Hz

Power Input 
85 to 250 V AC 
100 to 330 V DC 
Max 10 A 
Frequency 47/63 Hz

| Power Supply AMT205 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power supply range |  |  |  |  | 85-240 VAC or 100-330VDC |  |  |  |  |
| Input frequency range |  |  |  |  | 47-63 Hz |  |  |  |  |
| Consumption |  |  |  |  | up to 3 KVA |  |  |  |  |
| Nominal current |  |  |  |  | 5 A at 230 VAC |  |  |  |  |
| Connection |  |  |  |  | According to IEC60320 |  |  |  |  |
| High Voltage, Low Current Generators AMT205 (Input Voltage≥ 220V) |  |  |  |  |  |  |  |  |  |
| Voltage |  | 6 Phase (L-N) |  |  | AC: 6 X 0 ... 300 V |  |  |  |  |
|  |  |  |  |  | DC: 6 X 0 ... 420 V |  |  |  |  |
|  |  | Series and parallel |  |  | Yes |  |  |  |  |
|  |  | Resolution |  |  | 20 μV |  |  |  |  |
|  |  | Accuracy |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |  |  |
|  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |  |  |
| Current |  | Normal Mode |  |  | 6 Phase (L-N) |  |  | AC: 6 X 0 ... 0.25 A |  |
|  |  |  |  |  |  |  |  | DC: 6 X 0 ... 0.4 A |  |
|  |  | Internal Booster Mode time<200ms |  |  | 6 Phase (L-N) |  |  | AC: 6 X 0 ... 0.85 A |  |
|  |  |  |  |  |  |  |  | DC: 6 X 0 ... 1.2 A |  |
|  |  | Series and parallel |  |  |  | Yes |  |  |  |
|  |  | Resolution |  |  |  | 20 μA |  |  |  |
|  |  | Accuracy |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |  |
|  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |  |
| Phase |  | Range |  |  |  | 0° to 360° |  |  |  |
|  |  | Resolution |  |  |  | 1μ° |  |  |  |
|  |  | Accuracy |  |  |  | Guar.: 0.1° |  |  |  |
|  |  |  |  |  |  | Typ.: 0.01° |  |  |  |
| Frequency |  | Range |  |  |  | 0 ... 5 kHz |  |  |  |
|  |  | Resolution |  |  |  | 1 μHz |  |  |  |
|  |  | Accuracy |  |  |  | Guar.: 10 μHz , Typ.: 1 μHz |  |  |  |
| Power |  | 250 300 200 100 150 50 0 V(V) P(W) 50 100 150 200 250 300 0 |  |  |  |  |  |  |  |
| Harmonic Injection |  |  |  | Enter Harmonic |  | Yes |  |  | 2 Free Harmonic |
|  |  |  |  | Harmonic Order |  | No |  |  |  |
| Recording |  |  |  | Sampling Rate |  | 1.2 ms |  |  |  |
|  |  |  |  | Variable |  | Currents and Voltages |  |  |  |
| Protection |  |  |  | Detection |  | Power according to power curves |  |  |  |
|  |  |  |  |  |  | No |  |  |  |
|  |  |  |  | Type |  | Test o |  |  |  |
| Connection Banana Sockets |  |  |  | 4 mm (0.16 in) banana sockets |  |  |  |  |  |
| Connection Combination Socket |  |  |  | Group A |  |  |  |  |  |
| LED |  |  |  | Green (1 Color) |  |  |  |  |  |
| Low Voltage, High Current Generators AMT205 |  |  |  |  |  |  |  |  |  |
| Current | Normal Mode |  | 6 Phase (L-N) |  |  |  | AC: 6 X 0 ... 32 A |  |  |
|  |  |  |  |  |  |  | DC: 6 X 0 ... 45 A |  |  |
|  |  |  | Resolution |  |  |  | 170 μA |  |  |
|  |  |  | Accuracy |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |
|  |  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg |  |  |
|  | Mode amplificateur interne temps < 300 ms |  | 6 Phase (L-N) |  |  |  | AC: 6 X 0 ... 67 A |  |  |
|  |  |  | Resolution |  |  |  | DC: 6 X 0 ... 95 A |  |  |
|  |  |  |  |  |  |  | 170 μA |  |  |
|  |  |  | Accuracy |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |
|  |  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |
|  | Maximum Compliance Voltage |  |  |  |  |  | 22V |  |  |
|  | Series and parallel |  |  |  |  |  | Yes |  |  |
| Voltage | 6 Phase (L-N) |  |  |  |  |  | AC: 6 X 0 ... 12 V |  |  |
|  |  |  |  |  |  |  | DC: 6 X 0 ... 20 V |  |  |
|  | Series and parallel |  |  |  |  |  | Yes |  |  |
|  | Resolution |  |  |  |  |  | 40 uV |  |  |
|  | Accuracy |  |  |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |
|  |  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |

| Power Supply AMT105 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power supply range |  |  |  | 85-240 VAC or 100-330VDC |  |  |  |  |
| Input frequency range |  |  |  | 47-63 Hz |  |  |  |  |
| Consumption |  |  |  | up to 2 KVA |  |  |  |  |
| Nominal current |  |  |  | 3 A at 230 VAC |  |  |  |  |
| Connection |  |  |  | According to IEC60320 |  |  |  |  |
| High Voltage, Low Current Generators AMT105 (Input Voltage≥ 220V) |  |  |  |  |  |  |  |  |
| Voltage |  | 6 Phase (L-N) |  | AC: 4 X 0 ... 150 V |  |  |  |  |
|  |  |  |  | DC: 4 X 0 ... 210 V |  |  |  |  |
|  |  | Series and parallel |  | Yes |  |  |  |  |
|  |  | Resolution |  | 400 μV |  |  |  |  |
|  |  | Accuracy |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |  |  |
|  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |  |  |
| Current |  | No |  |  |  |  |  |  |
| Phase |  | Range |  | 0° to 360° |  |  |  |  |
|  |  | Resolution |  | 1μ° |  |  |  |  |
|  |  | Accuracy |  | Guar.: 0.1° |  |  |  |  |
|  |  |  |  | Typ.: 0.01° |  |  |  |  |
| Frequency |  | Range |  | 0 ... 10 kHz |  |  |  |  |
|  |  | Resolution |  | 1 μHz |  |  |  |  |
|  |  | Accuracy |  | Guar.: 10 μHz , Typ.: 1 μHz |  |  |  |  |
| Power |  | 250 300 200 100 150 50 0 V(V) P(W) 50 100 150 200 250 300 0 |  |  |  |  |  |  |
| Harmonic Injection |  |  | Enter Harmonic |  | Yes |  |  | 2 Free Harmonic |
|  |  |  | Harmonic Order |  | No |  |  |  |
| Recording |  |  | Sampling Rate |  | 1.2 ms |  |  |  |
|  |  |  | Variable | Currents and Voltages |  |  |  |  |
| Protection |  |  | Detection | Power according to power curves |  |  |  |  |
|  |  |  |  | No |  |  |  |  |
|  |  |  | Type | Test o |  |  |  |  |
| Connection Banana Sockets |  |  | 4 mm (0.16 in) banana sockets |  |  |  |  |  |
| Connection Combination Socket |  |  | Group A |  |  |  |  |  |
| LED |  |  | Green (1 Color) |  |  |  |  |  |
| Low Voltage, High Current Generators AMT105 |  |  |  |  |  |  |  |  |
| Current | Normal Mode |  | 6 Phase (L-N) |  |  | AC: 6 X 0 ... 32 A |  |  |
|  |  |  |  |  |  | DC: 6 X 0 ... 32 A |  |  |
|  |  |  | Resolution |  |  | 85 μA |  |  |
|  |  |  | Accuracy |  |  | Guar.: 0.15% of rd. + 0.015% of rg |  |  |
|  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |
|  | Internal Booster Mode |  | No |  |  |  |  |  |
|  | Maximum Compliance Voltage |  |  |  |  |  | 12V |  |
|  | Series and parallel |  |  |  |  |  | Yes |  |
| Voltage | No |  |  |  |  |  |  |  |

| (continue) Low Voltage, High Current Generators AMT105 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phase |  | Range |  |  |  |  |  | 0° to 360° |  |
|  |  | Resolution |  |  |  |  |  | 1μ° |  |
|  |  | Accuracy |  |  |  |  |  | Guar.: 0.1° |  |
|  |  |  |  |  |  |  |  | Typ.: 0.01° |  |
| Frequency |  | Range |  |  |  |  |  | 0 ... 2.5 kHz |  |
|  |  | Resolution |  |  |  |  |  | 1 μHz |  |
|  |  | Accuracy |  |  |  |  |  | Guar.: 10 μHz |  |
|  |  |  |  |  |  |  |  | Typ.: 1 μHz |  |
| Recording |  | Sampling Rate |  |  |  |  |  | 1.2 ms |  |
|  |  | Variable |  |  |  |  |  | Currents |  |
| Protection |  | Detection |  | Maximum Neutral Current |  |  |  | 32A: Unlimited |  |
|  |  |  |  |  |  |  |  | 64 A: 3 s |  |
|  |  |  |  |  |  |  |  | 100 A: 300 ms |  |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |
|  |  | Type |  |  |  |  |  | Test off |  |
| Maximum Neutral Current |  | 4 mm (0.16 in) banana sockets / 32 A continuously |  |  |  |  |  |  |  |
| Connection Banana Sockets |  | Group A (30 A continuously max) |  |  |  |  |  |  |  |
| LED |  | Green (1 Color) |  |  |  |  |  |  |  |
| Harmonic Injection |  | Enter Harmonic |  |  |  |  | Yes | 2 Free Harmonic |  |
|  |  | Harmonic Order |  |  |  |  | No |  |  |
| Power |  | 60 35 25 30 20 10 15 5 0 I(A) S(VA) 0 |  |  |  |  |  |  |  |
| Number |  | 8 |  |  |  |  |  |  |  |
| Dry |  | Open Circuit Voltage |  |  |  |  | 5 V |  |  |
|  |  | Short Circuit Voltage |  |  |  |  | Soware controlled |  |  |
| Wet | Range 1: 0 ... ±4.5 V(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  |  | Resolution |  |  |  | 35 μV |
|  |  |  |  |  | Impedance |  |  |  | 493.75 KΩ |
|  | Range 1: 0 ... ±30 V(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  |  | Resolution |  |  |  | 250μV |
|  |  |  |  |  | Impedance |  |  |  | 414.783 KΩ |
|  | Range 1: 0 ... ±180 V(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  |  | Resolution |  |  |  | 1.5mV |
|  |  |  |  |  | Impedance |  |  |  | 405.267 KΩ |
|  | No |  |  |  |  |  |  |  |  |
| Recording | Sampling Rate |  |  |  |  |  | 12.5 μs |  |  |
| Protection | Detection |  |  |  |  |  | Over voltage |  |  |
|  | Setting |  |  |  |  |  | Soware Controlled: Time , Enable |  |  |
|  | Type |  |  |  |  |  | Test o, Change to Dry |  |  |
| Galvanic Isolation |  |  | 8 Group (1+1+1+1+1+1+1+1) |  |  |  |  |  |  |
| LED |  |  | Green (1 Color) |  |  |  |  |  |  |

| (continue) Low Voltage, High Current Generators AMT205 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phase |  | Range |  |  |  |  |  |  |  |  | 0° to 360° |
|  |  | Resolution |  |  |  |  |  |  |  |  | 1μ° |
|  |  | Accuracy |  |  |  |  |  |  |  |  | Guar.: 0.1° |
|  |  |  |  |  |  |  |  |  |  |  | Typ.: 0.01° |
| Frequency |  | Range |  |  |  |  |  |  |  |  | 0 ... 2.5 kHz |
|  |  | Resolution |  |  |  |  |  |  |  |  | 1 μHz |
|  |  | Accuracy |  |  |  |  |  |  |  |  | Guar.: 10 μHz |
|  |  |  |  |  |  |  |  |  |  |  | Typ.: 1 μHz |
| Recording |  | Sampling Rate |  |  |  |  |  |  |  |  | 1.2 ms |
|  |  | Variable |  |  |  |  |  |  |  |  | Currents & Voltages |
| Protection |  | Detection |  | Maximum Neutral Current |  |  |  |  |  |  | 32A: Unlimited |
|  |  |  |  |  |  |  |  |  |  |  | 64 A: 3 s |
|  |  |  |  |  |  |  |  |  |  |  | 100 A: 300 ms |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |  |  |
|  |  | Type |  |  |  |  |  |  |  |  | Test off |
| Maximum Neutral Current |  | 4 mm (0.16 in) banana sockets / 32 A continuously |  |  |  |  |  |  |  |  |  |
| Connection Banana Sockets |  | Group A (30 A continuously max) |  |  |  |  |  |  |  |  |  |
| LED |  | RGB (16 Million Color) |  |  |  |  |  |  |  |  |  |
| Harmonic Injection |  | Enter Harmonic |  |  |  |  | Yes | 2 Free Harmonic |  |  |  |
|  |  | Harmonic Order |  |  |  |  | Yes | Maximum Order 40 for 50Hz (2KHz) |  |  |  |
| Power |  | 5 10 15 20 25 30 60 35 0 I(A) S(VA) 0 |  |  |  |  |  |  |  |  |  |
| Number | 8 |  |  |  |  |  |  |  |  |  |  |
| Dry | Open Circuit Voltage |  |  |  |  |  |  | 5 V |  |  |  |
|  | Short Circuit Voltage |  |  |  |  |  |  | Soware controlled |  |  |  |
| Wet | Range 1: 0 ... ±4.5 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 35 μV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 493.75 KΩ |  |
|  | Range 1: 0 ... ±30 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 250μV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 414.783 KΩ |  |
|  | Range 1: 0 ... ±180 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 1.5mV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 405.267 KΩ |  |
|  | Range 1: 0 ... ±520 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 4mV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 404.298 KΩ |  |
| Recording | Sampling Rate |  |  |  |  |  |  |  | 12.5 μs |  |  |
| Protection | Detection |  |  |  |  |  |  |  | Over voltage |  |  |
|  | Setting |  |  |  |  |  |  |  | Soware Controlled: Time , Enable |  |  |
|  | Type |  |  |  |  |  |  |  | Test o, Change to Dry |  |  |
| Galvanic Isolation |  |  | 8 Group (1+1+1+1+1+1+1+1) |  |  |  |  |  |  |  |  |
| LED |  |  | RGB (16 Million Color) |  |  |  |  |  |  |  |  |

| Binary Outputs AMT105 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type | Electro mechanical relay contacts |  |  |  |  |  |  |  |  |
|  | - |  |  |  |  |  |  |  |  |
| Control | Soware controlled |  |  |  |  |  |  |  |  |
| Number | 4 |  |  |  |  |  |  |  |  |
| Maximum Voltage in open mode | Electro Mechanic |  |  |  | 750V (Rms) |  |  |  |  |
|  | No |  |  |  |  |  |  |  |  |
| Maximum Current | Electro Mechanic |  |  |  | 10A (Rms) |  |  |  |  |
|  | No |  |  |  |  |  |  |  |  |
| Break Capacity AC | Electro Mechanic |  |  |  | 2500 VA |  |  |  |  |
|  | No |  |  |  |  |  |  |  |  |
| Break Capacity DC | Electro Mechanic |  |  |  | 300 W |  |  |  |  |
|  | No |  |  |  |  |  |  |  |  |
| Recording | No |  |  |  |  |  |  |  |  |
| Protection | No |  |  |  |  |  |  |  |  |
| Galvanic Isolation | 4 Group (1+1+1+1) |  |  |  |  |  |  |  |  |
| LED | Green (1 Color) |  |  |  |  |  |  |  |  |
| AC/DC Current Measuring Input AMT105 |  |  |  |  |  |  |  |  |  |
| Range 2: 0 ... ± 800 mA |  | Accuracy |  |  |  |  | 0.05% of rg |  |  |
|  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |  |
|  |  | Resolution |  |  |  |  | 6 μA |  |  |
|  |  | Shunt |  |  |  |  | 1Ω |  |  |
| Range 3: 0 ... ± 35 mA |  | No |  |  |  |  |  |  |  |
| Range 1: 0 ... ± 10 A |  | No |  |  |  |  |  |  |  |
| Range 4: 0 ... ± 250 μA |  | No |  |  |  |  |  |  |  |
| Recording |  | Resolution |  |  |  | 400 μs |  |  |  |
| Protection |  | Accuracy |  |  |  | Overcurrent |  |  |  |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |
|  |  | Type |  |  |  | Test o, Change to open circuit |  |  |  |
| Galvanic Isolation |  | 1 Group |  |  |  |  |  |  |  |
| LED |  | Green (1 Color) |  |  |  |  |  |  |  |
| AC/DC Voltage Measuring Input AMT105 |  |  |  |  |  |  |  |  |  |
| Range 1: 0 ... ±400 mV(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |  |
|  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |
|  |  |  |  | Resolution |  |  |  | 3 μV |  |
|  |  |  |  | Impedance |  |  |  | 54.7826 KΩ |  |
| Range 2: 0 ... ±120 mV(Peak) |  |  |  | No |  |  |  |  |  |
| Range 1: 0 ... ±50 mV(Peak) |  |  |  | No |  |  |  |  |  |
| Range 2: 0 ... ±10 mV(Peak) |  |  |  | No |  |  |  |  |  |
| Recording |  |  |  | Sampling Rate |  |  |  | 400 μs |  |
| Protection |  |  |  | Detection |  |  |  | Over Voltage |  |
|  |  |  |  | Setting |  |  |  | Software Controlled: Time , Enable |  |
|  |  |  |  | Type |  |  |  | Test o |  |
| Galvanic Isolation |  |  |  | 1 Group |  |  |  |  |  |
| LED |  |  |  | Green (1 Color) |  |  |  |  |  |
| AUX. DC AMT105 |  |  |  |  |  |  |  |  |  |
| Aux. DC |  |  | Any combination of 12 channels |  |  |  |  |  | 0 ... 212 V |
|  |  |  |  |  |  |  |  |  | 0 ... 0.4 A |
| GPS AMT105 |  |  |  |  |  |  |  |  |  |
| Internal GPS Module |  |  | Yes |  |  |  |  |  |  |
| Accuracy |  |  | 8ns |  |  |  |  |  |  |
| Time To Lock |  |  | 10s |  |  |  |  |  |  |
| Delay Adjustment |  |  | Yes |  |  |  |  |  |  |

| Binary Outputs AMT205 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type | Electro mechanical relay contacts |  |  |  |  |  |  |  |  |
|  | Transistor |  |  |  |  |  |  |  |  |
| Control | Soware controlled |  |  |  |  |  |  |  |  |
| Number | 4 |  |  |  |  |  |  |  |  |
| Maximum Voltage in open mode | Electro Mechanic |  |  |  | 750V (Rms) |  |  |  |  |
|  | Transistor |  |  |  | 50 V |  |  |  |  |
| Maximum Current | Electro Mechanic |  |  |  | 10A (Rms) |  |  |  |  |
|  | Transistor |  |  |  | 50 mA |  |  |  |  |
| Break Capacity AC | Electro Mechanic |  |  |  | Smax |  |  |  | 2500 VA |
|  | Transistor |  |  |  | Smax |  |  |  | 2.5 VA |
| Break Capacity DC | Electro Mechanic |  |  |  | Pmax |  |  |  | 300 W |
|  | Transistor |  |  |  | Pmax |  |  |  | 2.5W |
| Recording | Sampling Rate |  |  |  | 50 μs |  |  |  |  |
|  | Resolution |  |  |  | 2 mA |  |  |  |  |
|  | Accuracy |  |  |  | 0.3 mA |  |  |  |  |
| Protection | Detection |  |  |  | Overcurrent |  |  |  |  |
|  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |  |
|  | Type |  |  |  | Test o, Open Relays |  |  |  |  |
| Galvanic Isolation | 4 Group (1+1+1+1) |  |  |  |  |  |  |  |  |
| LED | RGB (16 Million Color) |  |  |  |  |  |  |  |  |
| AC/DC Current Measuring Input AMT205 |  |  |  |  |  |  |  |  |  |
| Range 2: 0 ... ± 800 mA |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 6 μA |  |  |  |
|  |  | Shunt |  |  |  | 1Ω |  |  |  |
| Range 3: 0 ... ± 35 mA |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 0.3 μA |  |  |  |
|  |  | Shunt |  |  |  | 22Ω |  |  |  |
| Range 1: 0 ... ± 10 A |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 1.5mA |  |  |  |
|  |  | Shunt |  |  |  | 5mΩ |  |  |  |
| Range 4: 0 ... ± 82 μA |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 6 nA |  |  |  |
|  |  | Shunt |  |  |  | 3 KΩ |  |  |  |
| Recording |  | Resolution |  |  |  | 12.5 μs |  |  |  |
| Protection |  | Accuracy |  |  |  | Overcurrent |  |  |  |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |
|  |  | Type |  |  |  | Test o, Change to open circuit |  |  |  |
| Galvanic Isolation |  | 1 Group |  |  |  |  |  |  |  |
| LED |  | RGB (16 Million Color) |  |  |  |  |  |  |  |
| AC/DC Voltage Measuring Input AMT205 |  |  |  |  |  |  |  |  |  |
| Range 1: 0 ... ±400 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 3 μV |  |  |
|  |  |  |  | Impedance |  |  | 54.7826 KΩ |  |  |
| Range 2: 0 ... ±120 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 1 μV |  |  |
|  |  |  |  | Impedance |  |  | 133.75 KΩ |  |  |
| Range 1: 0 ... ±50 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 500 nV |  |  |
|  |  |  |  | Impedance |  |  | 54.7826 KΩ |  |  |
| Range 2: 0 ... ±10 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 100 nV |  |  |
|  |  |  |  | Impedance |  |  | 133.75 KΩ |  |  |
| Recording |  |  |  | Sampling Rate |  |  | 12.5 μs |  |  |
| Protection |  |  |  | Detection |  |  | Over Voltage |  |  |
|  |  |  |  | Setting |  |  | Software Controlled: Time , Enable |  |  |
|  |  |  |  | Type |  |  | Test o, Change to open circuit |  |  |
| Galvanic Isolation |  |  |  | 1 Group |  |  |  |  |  |
| LED |  |  |  | RGB (16 Million Color) |  |  |  |  |  |
| AUX. DC AMT205 |  |  |  |  |  |  |  |  |  |
| Aux. DC |  |  | Any combination of 12 channels |  |  |  |  | Max Voltage : 1200 V , 0.4 A |  |
|  |  |  |  |  |  |  |  | Max Current : 8 V , 210 A |  |
| GPS AMT205 |  |  |  |  |  |  |  |  |  |
| Internal GPS Module |  |  | Yes |  |  |  |  |  |  |
| Accuracy |  |  | 8ns |  |  |  |  |  |  |
| Time To Lock |  |  | 10s |  |  |  |  |  |  |
| Delay Adjustment |  |  | Yes |  |  |  |  |  |  |

| Protocol AMT105 |  |  |  |  |
| --- | --- | --- | --- | --- |
| IEC 61850 |  | GOOSE Publish |  | 10 |
|  |  | Goose Subscribe |  | 10 |
|  |  | Virtual Binary I/O |  | 32 IN / 32 OUT |
|  |  | SV Publish Streams |  | NO |
|  |  | SV Subscribe Streams |  | NO |
|  |  | SV Sample Rates |  | NO |
|  |  | Ethernet Ports |  | 1x RJ45 100Base |
|  |  | Time Sync |  | PPS |
|  |  | Time Accuracy |  | ±80 ns (PPS) |
| Combination Cable AMT105 |  |  |  |  |
| 3 Voltage, 3 Current |  | Yes |  |  |
| 6 Current |  | Yes |  |  |
| PC Connection AMT105 |  |  |  |  |
| Wifi |  | Yes |  |  |
| LED |  | 1 Port |  |  |
| Programming USB Port |  | No |  |  |
| Physical Characteristic AMT105 |  |  |  |  |
| Weight |  | 14kg |  |  |
| Dimension |  | 35cm-35cm-15cm |  |  |
| Operating Temperature |  | -10 to 55° C |  |  |
| Storage Temperature |  | -20 to 85° C |  |  |
| Humidity |  | 70% |  |  |
| Transformer Specification AMT105 |  |  |  |  |
| HV & LV outputs-power |  | Frequency |  |  |
|  |  | Power |  |  |
| HV & LV outputs-Voltage |  | 3-phase AC (RMS) |  | 0-150 V(LN)….550mA peak |
|  |  | 1-phase AC (RMS) |  | 0-450V(LN)….550 mA peak |
|  |  | 3-phase DC |  | 0-220V(LN)….550 mA |
|  |  | 1-phase DC |  | 0-630V(LN)….550mA peak |
| HV & LV outputs-Current |  | 3-phase AC (RMS) |  | 0-32A….12V |
|  |  | 1-phase AC (RMS) |  |  |
|  |  | 3-phase DC |  | 0-10A….12V |
|  |  | 1-phase DC |  | 0-10A….40V |
| HV & LV input-Voltage | AC(RMS) | 0 ... 400m V 0.01 % rd + 0.017 % range 0 ... 4.5 V 0.007 % rd + 0.012 % range 0 ... 30V 0.022 % rd + 0.032 % range 0 ... 188V 0.01 % rd + 0.017 % range |  |  |
|  | DC |  |  |  |
| HV & LV input-Current | AC(RMS) | 0 ... 800 mA 0.008 % rd + 0.01 % range |  |  |
|  | DC |  |  |  |
| Test Standard |  |  | IEC61869 / 60044 |  |
| Voltage Output Range |  |  | 0-450V |  |
| Current Output Range |  |  | 0-128A |  |
| Output Frequency Range |  |  | DC & 5-2500HZ |  |
| CT Ratio Measurement Accuracy |  |  | Ratio: 1-30000 accuracy: 0.2 |  |
| Phase displacement: Resolution Accuracy |  |  | 0.01 min 3 min (typical) / 5 min (guaranteed) |  |
| Minimum Knee Point |  |  | 0.5V |  |
| Maximum Knee Point |  |  | 4500V |  |
| "Winding Resistance Resolution Accuracy" |  |  | 1 mΩ 0.05 % (typical) / 0.1 % + 1 mΩ (guaranteed) |  |
| Current Input Range(CT Secondary Side) |  |  | 1mA - 500mA |  |
| Minimum Knee Current |  |  | 1mA |  |
| Maximum Knee Voltage |  |  | 1.5A Up to 4KV |  |

| Protocol AMT205 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| IEC 61850 | GOOSE Publish |  | 128 |  |  |  |  |
|  | Goose Subscribe |  | 128 |  |  |  |  |
|  | Virtual Binary I/O |  | 360 IN / 360 OUT |  |  |  |  |
|  | SV Publish Streams |  | 10 |  |  |  |  |
|  | SV Subscribe Streams |  | 10 |  |  |  |  |
|  | SV Sample Rates |  | 80-256 samples/cycle |  |  |  |  |
|  | Ethernet Ports |  | 3x RJ45 100Base , 1x External Fiber 100Base (Optional) |  |  |  |  |
|  | Time Sync |  | PTP (IEEE-1588), IRIG-B, PPS, SNTP |  |  |  |  |
|  | Time Accuracy |  | ±1 µs (PTP), ±80 ns (PPS) |  |  |  |  |
| Combination Cable AMT205 |  |  |  |  |  |  |  |
| 3 Voltage, 3 Current |  |  |  |  |  | Yes |  |
| 6 Current |  |  |  |  |  | No |  |
| PC Connection AMT205 |  |  |  |  |  |  |  |
| Wifi |  |  |  |  |  | Yes |  |
| LED |  |  |  |  |  | 1 Port |  |
| Programming USB Port |  |  |  |  |  | Yes |  |
| Physical Characteristic AMT205 |  |  |  |  |  |  |  |
| Weight |  |  |  |  |  | 14kg |  |
| Dimension |  |  |  |  |  | 35cm-35cm-15cm |  |
| Operating Temperature |  |  |  |  |  | -10 to 55° C |  |
| Storage Temperature |  |  |  |  |  | -20 to 85° C |  |
| Humidity |  |  |  |  |  | 70% |  |
| Transformer Specification AMT205 |  |  |  |  |  |  |  |
| HV & LV outputs-power |  |  |  |  | Frequency |  |  |
|  |  |  |  |  | Power |  |  |
| HV & LV outputs-Voltage |  |  |  |  | 3-phase AC (RMS) |  | 0-600 V(LN)….1.2 A peak |
|  |  |  |  |  | 1-phase AC (RMS) |  | 0-1200V(LN)….1.2 A peak |
|  |  |  |  |  | 3-phase DC |  | 0-850V(LN)….1.2 A |
|  |  |  |  |  | 1-phase DC |  | 0-1700V(LN)….1.2 A peak |
| HV & LV outputs-Current |  |  |  |  | 3-phase AC (RMS) |  | 0-32A….22V |
|  |  |  |  |  | 1-phase AC (RMS) |  |  |
|  |  |  |  |  | 3-phase DC |  | 0-10A….22V |
|  |  |  |  |  | 1-phase DC |  | 0-10A….60V |
| HV & LV input-Voltage |  | AC(RMS) |  |  | 0 ... 10 mV 0.022 % rd + 0.032 % range 0 ... 50 mV 0.01 % rd + 0.017 % range 0 ... 120m V 0.007 % rd + 0.012 % range 0 ... 400m V 0.01 % rd + 0.017 % range 0 ... 4.5 V 0.007 % rd + 0.012 % range 0 ... 30V 0.022 % rd + 0.032 % range 0 ... 188V 0.01 % rd + 0.017 % range 0 ... 520 V 0.007 % rd + 0.012 % range |  |  |
|  |  | DC |  |  |  |  |  |
| HV & LV input-Current |  | AC(RMS) |  |  | 0 …82 uA 0.1 % rd + 0.023 % range 0 ... 35 mA 0.037 % rd + 0.026 % range 0 ... 800 mA 0.008 % rd + 0.01 % range 0 ... 10 A 0.008 % rd + 0.01 % range |  |  |
|  |  | DC |  |  |  |  |  |
| Test Standard |  |  |  | IEC61869 / 60044 |  |  |  |
| Voltage Output Range |  |  |  | 0-1200V |  |  |  |
| Current Output Range |  |  |  | 0-128A |  |  |  |
| Output Frequency Range |  |  |  | DC & 5-2500HZ |  |  |  |
| CT Ratio Measurement Accuracy |  |  |  | Ratio: 1-30000 accuracy: 0.2 |  |  |  |
| Phase displacement: Resolution Accuracy |  |  |  | 0.01 min 3 min (typical) / 5 min (guaranteed) |  |  |  |
| Minimum Knee Point |  |  |  | 0.01V |  |  |  |
| Maximum Knee Point |  |  |  | 10KV |  |  |  |
| "Winding Resistance Resolution Accuracy" |  |  |  | 1 mΩ 0.05 % (typical) / 0.1 % + 1 mΩ (guaranteed) |  |  |  |
| Current Input Range(CT Secondary Side) |  |  |  | 1 mA - 7 A |  |  |  |
| Minimum Knee Current |  |  |  | 100uA |  |  |  |
| Maximum Knee Voltage |  |  |  | 10A up to 50V 2.5A Up to 10KV |  |  |  |

| PT SPECIFICATION AMT105 |  |
| --- | --- |
| Test Standard | IEC61869 / 60044 |
| Voltage Output Range | 0-450V AC |
| Current Output Range | 0-128A |
| Ratio Measurement Voltage Level Typical accuracy | Ratio: 1-500KV accuracy: 0.2 |
| Phase displacement measurement Voltage level Typical accuracy | 0.01 min 3 min (typical) / 5 min (guaranteed) |
| Winding Resistance: Resolution Guaranteed Accuracy Typical accuracy | 1 mΩ 0.1 % + 1 mΩ 0.05 % |

| PT SPECIFICATION AMT205 |  |
| --- | --- |
| Test Standard | IEC61869 / 60044 |
| Voltage Output Range | 0-1200 V AC |
| Current Output Range | 0-128A |
| Ratio Measurement Voltage Level Typical accuracy | Ratio: 1-500KV accuracy: 0.2 |
| Phase displacement measurement Voltage level Typical accuracy | 0.01 min 3 min (typical) / 5 min (guaranteed) |
| Winding Resistance: Resolution Guaranteed Accuracy Typical accuracy | 1 mΩ 0.1 % + 1 mΩ 0.05 % |

Electrical and Physical Specifications

AMT103

AMT203

4 Voltage Outputs

4 Binary Outputs

DC/AC Analog Input

Combination Connector

4 Binary Outputs

4 Voltage Outputs or 
3 Voltage Output & 1 DC Supply

DC/AC Analog Input

4 Multifunctional Inputs

3 Current Outputs

On/Off Key

On/Off Key

3 Current Outputs

Combination Connector

4 Multifunctional Inputs

Wifi Antenna

USB Host

RS232

Earth

USB Debug

LAN

LAN/Wifi Switching

USB

Gps

Earth

USB-A

Power Input 
85 to 250 V AC 
100 to 330 V DC 
Max 10 A 
Frequency 47/63 Hz

Power Input 
85 to 250 V AC 
100 to 330 V DC 
Max 10 A 
Frequency 47/63 Hz

| Power Supply AMT203 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power supply range |  |  |  |  | 85-240 VAC or 100-330VDC |  |  |  |  |
| Input frequency range |  |  |  |  | 47-63 Hz |  |  |  |  |
| Consumption |  |  |  |  | up to 3 KVA |  |  |  |  |
| Nominal current |  |  |  |  | 5 A at 230 VAC |  |  |  |  |
| Connection |  |  |  |  | According to IEC60320 |  |  |  |  |
| High Voltage, Low Current Generators AMT203 (Input Voltage≥ 220V) |  |  |  |  |  |  |  |  |  |
| Voltage |  | 6 Phase (L-N) |  |  | AC: 4 X 0 ... 300 V |  |  |  |  |
|  |  |  |  |  | DC: 4 X 0 ... 420 V |  |  |  |  |
|  |  | Series and parallel |  |  | Yes |  |  |  |  |
|  |  | Resolution |  |  | 20 μV |  |  |  |  |
|  |  | Accuracy |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |  |  |
|  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |  |  |
| Current |  | Normal Mode |  |  | 6 Phase (L-N) |  |  | AC: 4 X 0 ... 0.25 A |  |
|  |  |  |  |  |  |  |  | DC: 4 X 0 ... 0.4 A |  |
|  |  | Internal Booster Mode time<200ms |  |  | 6 Phase (L-N) |  |  | AC: 4 X 0 ... 0.85 A |  |
|  |  |  |  |  |  |  |  | DC: 4 X 0 ... 1.2 A |  |
|  |  | Series and parallel |  |  |  | Yes |  |  |  |
|  |  | Resolution |  |  |  | 20 μA |  |  |  |
|  |  | Accuracy |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |  |
|  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |  |
| Phase |  | Range |  |  |  | 0° to 360° |  |  |  |
|  |  | Resolution |  |  |  | 1μ° |  |  |  |
|  |  | Accuracy |  |  |  | Guar.: 0.1° |  |  |  |
|  |  |  |  |  |  | Typ.: 0.01° |  |  |  |
| Frequency |  | Range |  |  |  | 0 ... 5 kHz |  |  |  |
|  |  | Resolution |  |  |  | 1 μHz |  |  |  |
|  |  | Accuracy |  |  |  | Guar.: 10 μHz , Typ.: 1 μHz |  |  |  |
| Power |  | 250 300 200 100 150 50 0 V(V) P(W) 50 100 150 200 250 300 0 |  |  |  |  |  |  |  |
| Harmonic Injection |  |  |  | Enter Harmonic |  | Yes |  |  | 2 Free Harmonic |
|  |  |  |  | Harmonic Order |  | No |  |  |  |
| Recording |  |  |  | Sampling Rate |  | 1.2 ms |  |  |  |
|  |  |  |  | Variable |  | Currents and Voltages |  |  |  |
| Protection |  |  |  | Detection |  | Power according to power curves |  |  |  |
|  |  |  |  |  |  | No |  |  |  |
|  |  |  |  | Type |  | Test o |  |  |  |
| Connection Banana Sockets |  |  |  | 4 mm (0.16 in) banana sockets |  |  |  |  |  |
| Connection Combination Socket |  |  |  | Group A |  |  |  |  |  |
| LED |  |  |  | Green (1 Color) |  |  |  |  |  |
| Low Voltage, High Current Generators AMT203 |  |  |  |  |  |  |  |  |  |
| Current | Normal Mode |  | 6 Phase (L-N) |  |  |  | AC: 3 X 0 ... 32 A |  |  |
|  |  |  |  |  |  |  | DC: 3 X 0 ... 45 A |  |  |
|  |  |  | Resolution |  |  |  | 170 μA |  |  |
|  |  |  | Accuracy |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |
|  |  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg |  |  |
|  | Mode amplificateur interne temps < 300 ms |  | 6 Phase (L-N) |  |  |  | AC: 3 X 0 ... 67 A |  |  |
|  |  |  | Resolution |  |  |  | DC: 3 X 0 ... 95 A |  |  |
|  |  |  |  |  |  |  | 170 μA |  |  |
|  |  |  | Accuracy |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |
|  |  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |
|  | Maximum Compliance Voltage |  |  |  |  |  | 22V |  |  |
|  | Series and parallel |  |  |  |  |  | Yes |  |  |
| Voltage | 6 Phase (L-N) |  |  |  |  |  | AC: 3 X 0 ... 12 V |  |  |
|  |  |  |  |  |  |  | DC: 3 X 0 ... 20 V |  |  |
|  | Series and parallel |  |  |  |  |  | Yes |  |  |
|  | Resolution |  |  |  |  |  | 40 uV |  |  |
|  | Accuracy |  |  |  |  |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |
|  |  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |

| Power Supply AMT103 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power supply range |  |  |  | 85-240 VAC or 100-330VDC |  |  |  |  |
| Input frequency range |  |  |  | 47-63 Hz |  |  |  |  |
| Consumption |  |  |  | up to 2 KVA |  |  |  |  |
| Nominal current |  |  |  | 3 A at 230 VAC |  |  |  |  |
| Connection |  |  |  | According to IEC60320 |  |  |  |  |
| High Voltage, Low Current Generators AMT103 (Input Voltage≥ 220V) |  |  |  |  |  |  |  |  |
| Voltage |  | 6 Phase (L-N) |  | AC: 4 X 0 ... 150 V |  |  |  |  |
|  |  |  |  | DC: 4 X 0 ... 210 V |  |  |  |  |
|  |  | Series and parallel |  | Yes |  |  |  |  |
|  |  | Resolution |  | 400 μV |  |  |  |  |
|  |  | Accuracy |  | Guar.: 0.15% of rd. + 0.015% of rg. |  |  |  |  |
|  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |  |  |
| Current |  | No |  |  |  |  |  |  |
| Phase |  | Range |  | 0° to 360° |  |  |  |  |
|  |  | Resolution |  | 1μ° |  |  |  |  |
|  |  | Accuracy |  | Guar.: 0.1° |  |  |  |  |
|  |  |  |  | Typ.: 0.01° |  |  |  |  |
| Frequency |  | Range |  | 0 ... 10 kHz |  |  |  |  |
|  |  | Resolution |  | 1 μHz |  |  |  |  |
|  |  | Accuracy |  | Guar.: 10 μHz , Typ.: 1 μHz |  |  |  |  |
| Power |  | 250 300 200 100 150 50 0 V(V) P(W) 50 100 150 200 250 300 0 |  |  |  |  |  |  |
| Harmonic Injection |  |  | Enter Harmonic |  | Yes |  |  | 2 Free Harmonic |
|  |  |  | Harmonic Order |  | No |  |  |  |
| Recording |  |  | Sampling Rate |  | 1.2 ms |  |  |  |
|  |  |  | Variable | Currents and Voltages |  |  |  |  |
| Protection |  |  | Detection | Power according to power curves |  |  |  |  |
|  |  |  |  | No |  |  |  |  |
|  |  |  | Type | Test o |  |  |  |  |
| Connection Banana Sockets |  |  | 4 mm (0.16 in) banana sockets |  |  |  |  |  |
| Connection Combination Socket |  |  | Group A |  |  |  |  |  |
| LED |  |  | Green (1 Color) |  |  |  |  |  |
| Low Voltage, High Current Generators AMT103 |  |  |  |  |  |  |  |  |
| Current | Normal Mode |  | 6 Phase (L-N) |  |  | AC: 3 X 0 ... 32 A |  |  |
|  |  |  |  |  |  | DC: 3 X 0 ... 32 A |  |  |
|  |  |  | Resolution |  |  | 85 μA |  |  |
|  |  |  | Accuracy |  |  | Guar.: 0.15% of rd. + 0.015% of rg |  |  |
|  |  |  |  |  |  | Typ.: 0.05% of rd. + 0.005% of rg. |  |  |
|  | Internal Booster Mode |  | No |  |  |  |  |  |
|  | Maximum Compliance Voltage |  |  |  |  |  | 12V |  |
|  | Series and parallel |  |  |  |  |  | Yes |  |
| Voltage | No |  |  |  |  |  |  |  |

| (continue) Low Voltage, High Current Generators AMT103 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phase |  | Range |  |  |  |  |  | 0° to 360° |  |
|  |  | Resolution |  |  |  |  |  | 1μ° |  |
|  |  | Accuracy |  |  |  |  |  | Guar.: 0.1° |  |
|  |  |  |  |  |  |  |  | Typ.: 0.01° |  |
| Frequency |  | Range |  |  |  |  |  | 0 ... 2.5 kHz |  |
|  |  | Resolution |  |  |  |  |  | 1 μHz |  |
|  |  | Accuracy |  |  |  |  |  | Guar.: 10 μHz |  |
|  |  |  |  |  |  |  |  | Typ.: 1 μHz |  |
| Recording |  | Sampling Rate |  |  |  |  |  | 1.2 ms |  |
|  |  | Variable |  |  |  |  |  | Currents |  |
| Protection |  | Detection |  | Maximum Neutral Current |  |  |  | 32A: Unlimited |  |
|  |  |  |  |  |  |  |  | 64 A: 3 s |  |
|  |  |  |  |  |  |  |  | 100 A: 300 ms |  |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |
|  |  | Type |  |  |  |  |  | Test off |  |
| Maximum Neutral Current |  | 4 mm (0.16 in) banana sockets / 32 A continuously |  |  |  |  |  |  |  |
| Connection Banana Sockets |  | Group A (30 A continuously max) |  |  |  |  |  |  |  |
| LED |  | Green (1 Color) |  |  |  |  |  |  |  |
| Harmonic Injection |  | Enter Harmonic |  |  |  |  | Yes | 2 Free Harmonic |  |
|  |  | Harmonic Order |  |  |  |  | No |  |  |
| Power |  | 60 35 25 30 20 10 15 5 0 I(A) S(VA) 0 |  |  |  |  |  |  |  |
| Number |  | 4 |  |  |  |  |  |  |  |
| Dry |  | Open Circuit Voltage |  |  |  |  | 5 V |  |  |
|  |  | Short Circuit Voltage |  |  |  |  | Soware controlled |  |  |
| Wet | Range 1: 0 ... ±4.5 V(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  |  | Resolution |  |  |  | 35 μV |
|  |  |  |  |  | Impedance |  |  |  | 493.75 KΩ |
|  | Range 1: 0 ... ±30 V(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  |  | Resolution |  |  |  | 250μV |
|  |  |  |  |  | Impedance |  |  |  | 414.783 KΩ |
|  | Range 1: 0 ... ±180 V(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  |  | Resolution |  |  |  | 1.5mV |
|  |  |  |  |  | Impedance |  |  |  | 405.267 KΩ |
|  | No |  |  |  |  |  |  |  |  |
| Recording | Sampling Rate |  |  |  |  |  | 12.5 μs |  |  |
| Protection | Detection |  |  |  |  |  | Over voltage |  |  |
|  | Setting |  |  |  |  |  | Soware Controlled: Time , Enable |  |  |
|  | Type |  |  |  |  |  | Test o, Change to Dry |  |  |
| Galvanic Isolation |  |  | 4 Group (1+1+1+1) |  |  |  |  |  |  |
| LED |  |  | Green (1 Color) |  |  |  |  |  |  |

| (continue) Low Voltage, High Current Generators AMT203 |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Phase |  | Range |  |  |  |  |  |  |  |  | 0° to 360° |
|  |  | Resolution |  |  |  |  |  |  |  |  | 1μ° |
|  |  | Accuracy |  |  |  |  |  |  |  |  | Guar.: 0.1° |
|  |  |  |  |  |  |  |  |  |  |  | Typ.: 0.01° |
| Frequency |  | Range |  |  |  |  |  |  |  |  | 0 ... 2.5 kHz |
|  |  | Resolution |  |  |  |  |  |  |  |  | 1 μHz |
|  |  | Accuracy |  |  |  |  |  |  |  |  | Guar.: 10 μHz |
|  |  |  |  |  |  |  |  |  |  |  | Typ.: 1 μHz |
| Recording |  | Sampling Rate |  |  |  |  |  |  |  |  | 1.2 ms |
|  |  | Variable |  |  |  |  |  |  |  |  | Currents & Voltages |
| Protection |  | Detection |  | Maximum Neutral Current |  |  |  |  |  |  | 32A: Unlimited |
|  |  |  |  |  |  |  |  |  |  |  | 64 A: 3 s |
|  |  |  |  |  |  |  |  |  |  |  | 100 A: 300 ms |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |  |  |
|  |  | Type |  |  |  |  |  |  |  |  | Test off |
| Maximum Neutral Current |  | 4 mm (0.16 in) banana sockets / 32 A continuously |  |  |  |  |  |  |  |  |  |
| Connection Banana Sockets |  | Group A (30 A continuously max) |  |  |  |  |  |  |  |  |  |
| LED |  | RGB (16 Million Color) |  |  |  |  |  |  |  |  |  |
| Harmonic Injection |  | Enter Harmonic |  |  |  |  | Yes | 2 Free Harmonic |  |  |  |
|  |  | Harmonic Order |  |  |  |  | Yes | Maximum Order 40 for 50Hz (2KHz) |  |  |  |
| Power |  | 60 35 25 30 20 10 15 5 0 I(A) S(VA) 0 |  |  |  |  |  |  |  |  |  |
| Number | 4 |  |  |  |  |  |  |  |  |  |  |
| Dry | Open Circuit Voltage |  |  |  |  |  |  | 5 V |  |  |  |
|  | Short Circuit Voltage |  |  |  |  |  |  | Soware controlled |  |  |  |
| Wet | Range 1: 0 ... ±4.5 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 35 μV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 493.75 KΩ |  |
|  | Range 1: 0 ... ±30 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 250μV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 414.783 KΩ |  |
|  | Range 1: 0 ... ±180 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 1.5mV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 405.267 KΩ |  |
|  | Range 1: 0 ... ±520 V(Peak) |  |  |  | Accuracy |  |  |  |  | 0.05% of rg. |  |
|  |  |  |  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  |  |  |  | Resolution |  |  |  |  | 4mV |  |
|  |  |  |  |  | Impedance |  |  |  |  | 404.298 KΩ |  |
| Recording | Sampling Rate |  |  |  |  |  |  |  | 12.5 μs |  |  |
| Protection | Detection |  |  |  |  |  |  |  | Over voltage |  |  |
|  | Setting |  |  |  |  |  |  |  | Soware Controlled: Time , Enable |  |  |
|  | Type |  |  |  |  |  |  |  | Test o, Change to Dry |  |  |
| Galvanic Isolation |  |  | 4 Group (1+1+1+1) |  |  |  |  |  |  |  |  |
| LED |  |  | RGB (16 Million Color) |  |  |  |  |  |  |  |  |

| Binary Outputs AMT103 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type | Electro mechanical relay contacts |  |  |  |  |  |  |  |
|  | - |  |  |  |  |  |  |  |
| Control | Soware controlled |  |  |  |  |  |  |  |
| Number | 4 |  |  |  |  |  |  |  |
| Maximum Voltage in open mode | Electro Mechanic |  |  |  | 750V (Rms) |  |  |  |
|  | No |  |  |  |  |  |  |  |
| Maximum Current | Electro Mechanic |  |  |  | 10A (Rms) |  |  |  |
|  | No |  |  |  |  |  |  |  |
| Break Capacity AC | Electro Mechanic |  |  |  | 2500 VA |  |  |  |
|  | No |  |  |  |  |  |  |  |
| Break Capacity DC | Electro Mechanic |  |  |  | 300 W |  |  |  |
|  | No |  |  |  |  |  |  |  |
| Recording | No |  |  |  |  |  |  |  |
| Protection | No |  |  |  |  |  |  |  |
| Galvanic Isolation | 4 Group (1+1+1+1) |  |  |  |  |  |  |  |
| LED | Green (1 Color) |  |  |  |  |  |  |  |
| AC/DC Current Measuring Input AMT103 |  |  |  |  |  |  |  |  |
| Range 2: 0 ... ± 800 mA |  | Accuracy |  |  |  |  | 0.05% of rg |  |
|  |  | Accuracy (Avg) |  |  |  |  | 0.02% of rg. |  |
|  |  | Resolution |  |  |  |  | 6 μA |  |
|  |  | Shunt |  |  |  |  | 1Ω |  |
| Range 3: 0 ... ± 35 mA |  | No |  |  |  |  |  |  |
| Range 1: 0 ... ± 10 A |  | No |  |  |  |  |  |  |
| Range 4: 0 ... ± 250 μA |  | No |  |  |  |  |  |  |
| Recording |  | Resolution |  |  |  | 400 μs |  |  |
| Protection |  | Accuracy |  |  |  | Overcurrent |  |  |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |
|  |  | Type |  |  |  | Test o, Change to open circuit |  |  |
| Galvanic Isolation |  | 1 Group |  |  |  |  |  |  |
| LED |  | Green (1 Color) |  |  |  |  |  |  |
| AC/DC Voltage Measuring Input AMT103 |  |  |  |  |  |  |  |  |
| Range 1: 0 ... ±400 mV(Peak) |  |  |  | Accuracy |  |  |  | 0.05% of rg. |
|  |  |  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |
|  |  |  |  | Resolution |  |  |  | 3 μV |
|  |  |  |  | Impedance |  |  |  | 54.7826 KΩ |
| Range 2: 0 ... ±120 mV(Peak) |  |  |  | No |  |  |  |  |
| Range 1: 0 ... ±50 mV(Peak) |  |  |  | No |  |  |  |  |
| Range 2: 0 ... ±10 mV(Peak) |  |  |  | No |  |  |  |  |
| Recording |  |  |  | Sampling Rate |  |  |  | 400 μs |
| Protection |  |  |  | Detection |  |  |  | Over Voltage |
|  |  |  |  | Setting |  |  |  | Software Controlled: Time , Enable |
|  |  |  |  | Type |  |  |  | Test o |
| Galvanic Isolation |  |  |  | 1 Group |  |  |  |  |
| LED |  |  |  | Green (1 Color) |  |  |  |  |
| AUX. DC AMT103 |  |  |  |  |  |  |  |  |
| Aux. DC |  |  | No |  |  |  |  |  |
| GPS AMT103 |  |  |  |  |  |  |  |  |
| Internal GPS Module |  |  | Yes |  |  |  |  |  |
| Accuracy |  |  | 8ns |  |  |  |  |  |
| Time To Lock |  |  | 10s |  |  |  |  |  |
| Delay Adjustment |  |  | Yes |  |  |  |  |  |

| Binary Outputs AMT203 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type | Electro mechanical relay contacts |  |  |  |  |  |  |  |  |
|  | Transistor |  |  |  |  |  |  |  |  |
| Control | Soware controlled |  |  |  |  |  |  |  |  |
| Number | 4 |  |  |  |  |  |  |  |  |
| Maximum Voltage in open mode | Electro Mechanic |  |  |  | 750V (Rms) |  |  |  |  |
|  | Transistor |  |  |  | 50 V |  |  |  |  |
| Maximum Current | Electro Mechanic |  |  |  | 10A (Rms) |  |  |  |  |
|  | Transistor |  |  |  | 50 mA |  |  |  |  |
| Break Capacity AC | Electro Mechanic |  |  |  | Smax |  |  |  | 2500 VA |
|  | Transistor |  |  |  | Smax |  |  |  | 2.5 VA |
| Break Capacity DC | Electro Mechanic |  |  |  | Pmax |  |  |  | 300 W |
|  | Transistor |  |  |  | Pmax |  |  |  | 2.5W |
| Recording | Sampling Rate |  |  |  | 50 μs |  |  |  |  |
|  | Resolution |  |  |  | 2 mA |  |  |  |  |
|  | Accuracy |  |  |  | 0.3 mA |  |  |  |  |
| Protection | Detection |  |  |  | Overcurrent |  |  |  |  |
|  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |  |
|  | Type |  |  |  | Test o, Open Relays |  |  |  |  |
| Galvanic Isolation | 4 Group (1+1+1+1) |  |  |  |  |  |  |  |  |
| LED | RGB (16 Million Color) |  |  |  |  |  |  |  |  |
| AC/DC Current Measuring Input AMT203 |  |  |  |  |  |  |  |  |  |
| Range 2: 0 ... ± 800 mA |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 6 μA |  |  |  |
|  |  | Shunt |  |  |  | 1Ω |  |  |  |
| Range 3: 0 ... ± 35 mA |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 0.3 μA |  |  |  |
|  |  | Shunt |  |  |  | 22Ω |  |  |  |
| Range 1: 0 ... ± 10 A |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 1.5mA |  |  |  |
|  |  | Shunt |  |  |  | 5mΩ |  |  |  |
| Range 4: 0 ... ± 82 μA |  | Accuracy |  |  |  | 0.05% of rg |  |  |  |
|  |  | Accuracy (Avg) |  |  |  | 0.02% of rg. |  |  |  |
|  |  | Resolution |  |  |  | 6 nA |  |  |  |
|  |  | Shunt |  |  |  | 3 KΩ |  |  |  |
| Recording |  | Resolution |  |  |  | 12.5 μs |  |  |  |
| Protection |  | Accuracy |  |  |  | Overcurrent |  |  |  |
|  |  | Setting |  |  |  | Soware Controlled: Time , Enable |  |  |  |
|  |  | Type |  |  |  | Test o, Change to open circuit |  |  |  |
| Galvanic Isolation |  | 1 Group |  |  |  |  |  |  |  |
| LED |  | RGB (16 Million Color) |  |  |  |  |  |  |  |
| AC/DC Voltage Measuring Input AMT203 |  |  |  |  |  |  |  |  |  |
| Range 1: 0 ... ±400 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 3 μV |  |  |
|  |  |  |  | Impedance |  |  | 54.7826 KΩ |  |  |
| Range 2: 0 ... ±120 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 1 μV |  |  |
|  |  |  |  | Impedance |  |  | 133.75 KΩ |  |  |
| Range 1: 0 ... ±50 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 500 nV |  |  |
|  |  |  |  | Impedance |  |  | 54.7826 KΩ |  |  |
| Range 2: 0 ... ±10 mV(Peak) |  |  |  | Accuracy |  |  | 0.05% of rg. |  |  |
|  |  |  |  | Accuracy (Avg) |  |  | 0.02% of rg. |  |  |
|  |  |  |  | Resolution |  |  | 100 nV |  |  |
|  |  |  |  | Impedance |  |  | 133.75 KΩ |  |  |
| Recording |  |  |  | Sampling Rate |  |  | 12.5 μs |  |  |
| Protection |  |  |  | Detection |  |  | Over Voltage |  |  |
|  |  |  |  | Setting |  |  | Software Controlled: Time , Enable |  |  |
|  |  |  |  | Type |  |  | Test o, Change to open circuit |  |  |
| Galvanic Isolation |  |  |  | 1 Group |  |  |  |  |  |
| LED |  |  |  | RGB (16 Million Color) |  |  |  |  |  |
| AUX. DC AMT203 |  |  |  |  |  |  |  |  |  |
| Aux. DC |  |  | Any combination of 4 channels |  |  |  |  | Max Voltage : 1200 V , 0.4 A |  |
|  |  |  |  |  |  |  |  | Max Current : 8 V , 210 A |  |
| GPS AMT203 |  |  |  |  |  |  |  |  |  |
| Internal GPS Module |  |  | Yes |  |  |  |  |  |  |
| Accuracy |  |  | 8ns |  |  |  |  |  |  |
| Time To Lock |  |  | 10s |  |  |  |  |  |  |
| Delay Adjustment |  |  | Yes |  |  |  |  |  |  |

| Protocol AMT103 |  |  |  |  |
| --- | --- | --- | --- | --- |
| IEC 61850 |  | GOOSE Publish |  | 10 |
|  |  | Goose Subscribe |  | 10 |
|  |  | Virtual Binary I/O |  | 32 IN / 32 OUT |
|  |  | SV Publish Streams |  | NO |
|  |  | SV Subscribe Streams |  | NO |
|  |  | SV Sample Rates |  | NO |
|  |  | Ethernet Ports |  | 1x RJ45 100Base |
|  |  | Time Sync |  | PPS |
|  |  | Time Accuracy |  | ±80 ns (PPS) |
| Combination Cable AMT103 |  |  |  |  |
| 3 Voltage, 3 Current |  | Yes |  |  |
| 6 Current |  | Yes |  |  |
| PC Connection AMT103 |  |  |  |  |
| Wifi |  | Yes |  |  |
| LED |  | 1 Port |  |  |
| Programming USB Port |  | No |  |  |
| Physical Characteristic AMT103 |  |  |  |  |
| Weight |  | 14kg |  |  |
| Dimension |  | 35cm-35cm-15cm |  |  |
| Operating Temperature |  | -10 to 55° C |  |  |
| Storage Temperature |  | -20 to 85° C |  |  |
| Humidity |  | 70% |  |  |
| Transformer Specification AMT103 |  |  |  |  |
| HV & LV outputs-power |  | Frequency |  |  |
|  |  | Power |  |  |
| HV & LV outputs-Voltage |  | 3-phase AC (RMS) |  | 0-150 V(LN)….550mA peak |
|  |  | 1-phase AC (RMS) |  | 0-450V(LN)….550 mA peak |
|  |  | 3-phase DC |  | 0-220V(LN)….550 mA |
|  |  | 1-phase DC |  | 0-630V(LN)….550mA peak |
| HV & LV outputs-Current |  | 3-phase AC (RMS) |  | 0-32A….12V |
|  |  | 1-phase AC (RMS) |  |  |
|  |  | 3-phase DC |  | 0-10A….12V |
|  |  | 1-phase DC |  | 0-10A….40V |
| HV & LV input-Voltage | AC(RMS) | 0 ... 400m V 0.01 % rd + 0.017 % range 0 ... 4.5 V 0.007 % rd + 0.012 % range 0 ... 30V 0.022 % rd + 0.032 % range 0 ... 188V 0.01 % rd + 0.017 % range |  |  |
|  | DC |  |  |  |
| HV & LV input-Current | AC(RMS) | 0 ... 800 mA 0.008 % rd + 0.01 % range |  |  |
|  | DC |  |  |  |
| Test Standard |  |  | IEC61869 / 60044 |  |
| Voltage Output Range |  |  | 0-450V |  |
| Current Output Range |  |  | 0-128A |  |
| Output Frequency Range |  |  | DC & 5-2500HZ |  |
| CT Ratio Measurement Accuracy |  |  | Ratio: 1-30000 accuracy: 0.2 |  |
| Phase displacement: Resolution Accuracy |  |  | 0.01 min 3 min (typical) / 5 min (guaranteed) |  |
| Minimum Knee Point |  |  | 0.5V |  |
| Maximum Knee Point |  |  | 4500V |  |
| "Winding Resistance Resolution Accuracy" |  |  | 1 mΩ 0.05 % (typical) / 0.1 % + 1 mΩ (guaranteed) |  |
| Current Input Range(CT Secondary Side) |  |  | 1mA - 500mA |  |
| Minimum Knee Current |  |  | 1mA |  |
| Maximum Knee Voltage |  |  | 1.5A Up to 4KV |  |

| Protocol AMT203 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| IEC 61850 | GOOSE Publish |  | 128 |  |  |  |  |
|  | Goose Subscribe |  | 128 |  |  |  |  |
|  | Virtual Binary I/O |  | 360 IN / 360 OUT |  |  |  |  |
|  | SV Publish Streams |  | 10 |  |  |  |  |
|  | SV Subscribe Streams |  | 10 |  |  |  |  |
|  | SV Sample Rates |  | 80-256 samples/cycle |  |  |  |  |
|  | Ethernet Ports |  | 3x RJ45 100Base , 1x External Fiber 100Base (Optional) |  |  |  |  |
|  | Time Sync |  | PTP (IEEE-1588), IRIG-B, PPS, SNTP |  |  |  |  |
|  | Time Accuracy |  | ±1 µs (PTP), ±80 ns (PPS) |  |  |  |  |
| Combination Cable AMT203 |  |  |  |  |  |  |  |
| 3 Voltage, 3 Current |  |  |  |  |  | Yes |  |
| 6 Current |  |  |  |  |  | No |  |
| PC Connection AMT203 |  |  |  |  |  |  |  |
| Wifi |  |  |  |  |  | Yes |  |
| LED |  |  |  |  |  | 1 Port |  |
| Programming USB Port |  |  |  |  |  | Yes |  |
| Physical Characteristic AMT203 |  |  |  |  |  |  |  |
| Weight |  |  |  |  |  | 14kg |  |
| Dimension |  |  |  |  |  | 35cm-35cm-15cm |  |
| Operating Temperature |  |  |  |  |  | -10 to 55° C |  |
| Storage Temperature |  |  |  |  |  | -20 to 85° C |  |
| Humidity |  |  |  |  |  | 70% |  |
| Transformer Specification AMT203 |  |  |  |  |  |  |  |
| HV & LV outputs-power |  |  |  |  | Frequency |  |  |
|  |  |  |  |  | Power |  |  |
| HV & LV outputs-Voltage |  |  |  |  | 3-phase AC (RMS) |  | 0-600 V(LN)….1.2 A peak |
|  |  |  |  |  | 1-phase AC (RMS) |  | 0-1200V(LN)….1.2 A peak |
|  |  |  |  |  | 3-phase DC |  | 0-850V(LN)….1.2 A |
|  |  |  |  |  | 1-phase DC |  | 0-1700V(LN)….1.2 A peak |
| HV & LV outputs-Current |  |  |  |  | 3-phase AC (RMS) |  | 0-32A….22V |
|  |  |  |  |  | 1-phase AC (RMS) |  |  |
|  |  |  |  |  | 3-phase DC |  | 0-10A….22V |
|  |  |  |  |  | 1-phase DC |  | 0-10A….60V |
| HV & LV input-Voltage |  | AC(RMS) |  |  | 0 ... 10 mV 0.022 % rd + 0.032 % range 0 ... 50 mV 0.01 % rd + 0.017 % range 0 ... 120m V 0.007 % rd + 0.012 % range 0 ... 400m V 0.01 % rd + 0.017 % range 0 ... 4.5 V 0.007 % rd + 0.012 % range 0 ... 30V 0.022 % rd + 0.032 % range 0 ... 188V 0.01 % rd + 0.017 % range 0 ... 520 V 0.007 % rd + 0.012 % range |  |  |
|  |  | DC |  |  |  |  |  |
| HV & LV input-Current |  | AC(RMS) |  |  | 0 …82 uA 0.1 % rd + 0.023 % range 0 ... 35 mA 0.037 % rd + 0.026 % range 0 ... 800 mA 0.008 % rd + 0.01 % range 0 ... 10 A 0.008 % rd + 0.01 % range |  |  |
|  |  | DC |  |  |  |  |  |
| Test Standard |  |  |  | IEC61869 / 60044 |  |  |  |
| Voltage Output Range |  |  |  | 0-1200V |  |  |  |
| Current Output Range |  |  |  | 0-128A |  |  |  |
| Output Frequency Range |  |  |  | DC & 5-2500HZ |  |  |  |
| CT Ratio Measurement Accuracy |  |  |  | Ratio: 1-30000 accuracy: 0.2 |  |  |  |
| Phase displacement: Resolution Accuracy |  |  |  | 0.01 min 3 min (typical) / 5 min (guaranteed) |  |  |  |
| Minimum Knee Point |  |  |  | 0.01V |  |  |  |
| Maximum Knee Point |  |  |  | 10KV |  |  |  |
| "Winding Resistance Resolution Accuracy" |  |  |  | 1 mΩ 0.05 % (typical) / 0.1 % + 1 mΩ (guaranteed) |  |  |  |
| Current Input Range(CT Secondary Side) |  |  |  | 1 mA - 7 A |  |  |  |
| Minimum Knee Current |  |  |  | 100uA |  |  |  |
| Maximum Knee Voltage |  |  |  | 10A up to 50V 2.5A Up to 10KV |  |  |  |

| PT SPECIFICATION AMT103 |  |
| --- | --- |
| Test Standard | IEC61869 / 60044 |
| Voltage Output Range | 0-450V AC |
| Current Output Range | 0-128A |
| Ratio Measurement Voltage Level Typical accuracy | Ratio: 1-500KV accuracy: 0.2 |
| Phase displacement measurement Voltage level Typical accuracy | 0.01 min 3 min (typical) / 5 min (guaranteed) |
| Winding Resistance: Resolution Guaranteed Accuracy Typical accuracy | 1 mΩ 0.1 % + 1 mΩ 0.05 % |

| PT SPECIFICATION AMT203 |  |
| --- | --- |
| Test Standard | IEC61869 / 60044 |
| Voltage Output Range | 0-1200 V AC |
| Current Output Range | 0-128A |
| Ratio Measurement Voltage Level Typical accuracy | Ratio: 1-500KV accuracy: 0.2 |
| Phase displacement measurement Voltage level Typical accuracy | 0.01 min 3 min (typical) / 5 min (guaranteed) |
| Winding Resistance: Resolution Guaranteed Accuracy Typical accuracy | 1 mΩ 0.1 % + 1 mΩ 0.05 % |